## INPUT
INPUTS | NOTES
Run Status | Set to 0 to disable a round while preserving setting records | 1 | 0
INPUT FILES | This section enables the specification of the required file locations
Project No. | Enter the 4 digit project #### | 1234 | 1234
Stage No. | Enter the 1 digit stage # | 0 | 0
File Path | The complete path to the directory containing your input files | C:\myproject | C:\myproject
Output Folder | The name of the output folder for storing simulation results, located within the specified File Path | DYR_RESULTS | DYR_RESULTS
Facility Model | Accept any of the following file types: .idv, .raw, .sav of the complete test model or up to the Point of Connection (POC). | myproject.sav | myproject.idv
Insert SMIB? | The program will insert SMIB to the most upstream bus of your facility | 0 | 1
DYR Model | Accept : .dyr | myproject.dyr | myproject.dyr
BASIC SIMULATION SETUP
Simulation Time Step | Simulation time step in seconds | 0.0041667 | 0.0041667
Simulation Duration | Minimum simulation duration in seconds | 20 | 20
System transformer voltage lower bound | This is used to identify the Point of Connection (POC), defined as the high-voltage side of the system transformer for the facility under test. Specify the lower bound in kV. | 69 | 69
System transformer voltage upper bound | This is used to identify the Point of Connection (POC), defined as the high-voltage side of the system transformer for the facility under test. Specify the higher bound in kV. | 500 | 500
Enable Setup | Set to 1 to enable the following settings or 0 to disable them if a test case is already available. If this is disabled, Insert SMIB will be automatically disabled. | 1 | 1
GEN P% | Initial Pgen as a percentage of Pmax (+) A machine with Pmin >= 0 is treated as a regular GEN | 1 | 1
BESS P% | Initial Pgen as a percentage of the Pmax (+), Pmin (-) A machine with Pmin < 0 and Pmax > 0 is treated as a BESS | 1 | 1
MOTOR P% | Initial Pgen as a percentage of Pmin (-) A machine with Pmin < 0 and Pmax = 0 is treated as a Motor | 1
Inf Bus Voltage | Initial voltage of the infinite bus. This may be set to the nominal voltage specific to the service area (i.e. For service areas with a voltage level of 144 kV, set it to 144 / 138 = 1.043 | 1 | 1
Interconnection Line Impedance | The impedance of the line between the high side of the system transformer and the tap point is defined here. A value of 0 indicates that no line is required for the tests, typically applicable to conventional machines or DERs. For IBRs, if the exact impedance is unavailable, a default value of 0.01 may be used. | 0 | 0.01
TESTS | Enter '1' for each test below that needs to be run. The voltage and frequency profile tab is assigned and can be modified as needed. - For the Fault Recovery (FR) Test, enter the system equivalent reactance for the zero impedance tie line in per unit (pu) and the fault duration in seconds within square brackets. The system equivalent reactance should be determined using the latest PBCS or OPBC case. If this information is unavailable, it may be approximated using SCR = 3 for IBRs or SCR = 5 for conventional generators, using the following formula: X_pu = 1/ (SCR X P_pu) where P_pu is the maximum active power output of the tested power plant at the Point of Connection (POC), based on a 100MVA base. - For the Short Circuit Ratio (SCR) Test, enter the SCR values within square brackets. Note this test only applies to IBRs. - For the Reference Step Change (RSC) Test, enter the reference type (VOLT-RSC, or FREQ-RSC) in quotations, the system equivalent impedance for the zero impedance tie line in per unit (pu), and the step change percentage within square brackets. The system equivalent reactance can be estimated using the same method as the FR Test. Note these tests only apply to IBRs. Add more tests by inserting rows within this section.
FS | FS | 1 | 1
FREQ | FRQ-STEP-UP | 1
FREQ | FRQ-STEP-DOWN | 1
VOLT | VLT-STEP-UP | 1 | 1
VOLT | VLT-STEP-DOWN | 1 | 1
VOLT | HVRT-IBR | 1 | 1
VOLT | LVRT-IBR | 1 | 1
FREQ | HFRT-IBR | 1
FREQ | LFRT-IBR | 1
FR | [0.1, 0.066667] | 1 | 1
SCR | [8,5,3,2,1.9,1.7,1.5,1.3] | 1 | 1
RSC | ['VOLT-RSC', 0.01, 0.05] | 1 | 1
RSC | ['FREQ-RSC', 0.01, 0.05] | 1
EXPORT | The following files will be automatically saved: the test case in .raw or .sav, result plots in a .pdf file, and simulation data in .out format. Additionally, you have the option to save the data in .csv format.
.csv | dynamic simulation results | 1 | 1
image | dynamic simulation result plots | 1 | 1

## FRQ-STEP-UP
Time (sec) | Voltage (p.u.) | Frequency (Hz)
0 | 1 | 60
5 | 1 | 60
5 | 1 | 60.3
25 | 1 | 60.3

## FRQ-STEP-DOWN
Time (sec) | Voltage (p.u.) | Frequency (Hz)
0 | 1 | 60
4.999 | 1 | 60
5 | 1 | 60
5 | 1 | 59.7
25 | 1 | 59.7

## VLT-STEP-UP
Time (sec) | Voltage (p.u.) | Frequency (Hz)
0 | 1 | 60
5 | 1 | 60
5 | 1.05 | 60
25 | 1.05 | 60

## VLT-STEP-DOWN
Time (sec) | Voltage (p.u.) | Frequency (Hz)
0 | 1 | 60
5 | 1 | 60
5 | 0.95 | 60
25 | 0.95 | 60

## HVRT
Time (sec) | Voltage (pu) | Frequency (Hz)
-0.001 | 1 | 60
0 | 1 | 60
5 | 1 | 60
5 | 1.2 | 60
5.2 | 1.2 | 60
5.2 | 1.175 | 60
5.5 | 1.175 | 60
5.5 | 1.15 | 60
8 | 1.15 | 60
8 | 1.1 | 60
20 | 1.1 | 60

## HVRT-IBR
Time (sec) | Voltage (pu) | Frequency (Hz) | Note: Time interval based on 502.1 requirements (e.g., instantaneous trip, 0.2s, 0.5s, 1s, continuous operation)
0 | 1 | 60
5 | 1 | 60
5 | 1.25 | 60
5.1 | 1.25 | 60
5.1 | 1.15 | 60
6.1 | 1.15 | 60
6.1 | 1.1 | 60
20 | 1.1 | 60

## LVRT
Time (sec) | Voltage (pu) | Frequency (Hz)
-0.001 | 1 | 60
0 | 1 | 60
5 | 1 | 60
5 | 0 | 60
5.15 | 0 | 60
5.15 | 0.45 | 60
5.3 | 0.45 | 60
5.3 | 0.65 | 60
7 | 0.65 | 60
7 | 0.75 | 60
8 | 0.75 | 60
8 | 0.9 | 60
20 | 0.9 | 60

## LVRT-IBR
Time (sec) | Voltage (pu) | Frequency (Hz) | Note: Time interval based on 502.1 requirements (e.g., 0.15s, 0.30s, 2.00s, 3.00s, continuous operation)
0 | 1 | 60
5 | 1 | 60
5 | 0.1 | 60
5.16 | 0.1 | 60
5.16 | 0.25 | 60
6.2 | 0.25 | 60
6.2 | 0.5 | 60
7.5 | 0.5 | 60
7.5 | 0.7 | 60
8 | 0.7 | 60
8 | 0.9 | 60
20 | 0.9 | 60

## HFRT
Time (sec) | Voltage (p.u.) | Frequency (Hz)
0 | 1 | 60
5 | 1 | 60
5 | 1 | 61.7
35 | 1 | 61.7
35 | 1 | 61.6
185 | 1 | 61.6
185 | 1 | 60.6
400 | 1 | 60.6

## HFRT-IBR
Time (sec) | Voltage (p.u.) | Frequency (Hz)
0 | 1 | 60
5 | 1 | 60
5 | 1 | 61.8
305 | 1 | 61.8
305 | 1 | 61.2
400 | 1 | 61.2

## LFRT
Time (sec) | Voltage (p.u.) | Frequency (Hz)
0 | 1 | 60
5 | 1 | 60
5 | 1 | 57
5.75 | 1 | 57
5.75 | 1 | 57.3
12.5 | 1 | 57.3
12.5 | 1 | 57.8
35 | 1 | 57.8
35 | 1 | 58.4
185 | 1 | 58.4
185 | 1 | 59.4
400 | 1 | 59.4

## LFRT-IBR
Time (sec) | Voltage (p.u.) | Frequency (Hz)
0 | 1 | 60
5 | 1 | 60
5 | 1 | 57
305 | 1 | 57
305 | 1 | 58.8
400 | 1 | 58.8