## UFLS Entity Contact
X
Appendix 1
PRC-006-AB-3 Underfrequency Load Shedding Criterion
UFLS Entity Data Submittals Requirements
Compliance with the Alberta Underfrequency Load Shedding Program
Category: |  |  |  | Generator | UFLS Entity
Company Name:
Respondent's Name:
Position/Title:
E-mail:
Phone Number:
Fax Number:
Address:
Submittal Date:
Are you an applicable entity per PRC-006-AB-3? |  |  |  |  | YES | (YES, NO) | YES

## Tab 2 - Detail Load
Notes: 1. Market Participants do not need to enter info. for greyed out areas; 2. This page is for System Peak Condition. 3. For clarity on the "reset freq. (Hz)": this depends on detailed relay setting, especially for the time delayed uderfrequency load shed blocks. For example, when frequency goes down to the triggering frequency (e.g. below 59.5Hz of the D2 block), the D2 block timer starts. But before D2 timer reaches the 30 sec threshold, system frequency recovers to or above the reset frequency, it will reset the D2 block timer. This parameter is not modelled in uderfrequency load shed model used for WECC/AESO system studies, but the information is required by WECC. 4. For clarity on the "Manual Restore Delay Time (Min)": manual restoration of tripped breakers is coordinated with the AESO System Controllers. If entities have plan to manually restore load, WECC/AESO needs to know the delay time. Otherwise, N/A may be acceptable too. 5. The question below regarding whether frequency relays operate above 80% of nominal is for information purpose only.
UNDER FREQUENCY LOAD SHED
UFLS SCHEDULE (Year) __________
DFO Total load ___ MW at system peak
Total System Peak in (Year): ___________ MW
|  | UF Block # | Substation (Element Tripped) | Breaker Number(s) | Substation Name or Line From |  | Line To |  | WECC Zone | WECC Area | Trip Freq. (Hz) | Reset Freq. (Hz) | Trip Time Delay (sec) | Breaker Time (cycles) | Total Tripping Time | Manual Restore Delay Time (Min) | Load Shed MW
[5 empty] | WECC Bus Name | WECC Bus # | WECC Bus Name | WECC Bus #
|  | 1 | [8 empty] | 59.1
|  | 1 | [8 empty] | 59.1
|  | 1 | [8 empty] | 59.1
|  | 1 | [8 empty] | 59.1
|  | 1 | [8 empty] | 59.1
|  | 1 | [8 empty] | 59.1
[5 empty] | Req. MW Load Shed for Block #1 | [7 empty] | Block #1 Total MW Load Shed
[5 empty] | Req. % Load Shed for Block #1 | [7 empty] | Block #1 % Load Shed
Note:
|  | 2 | [8 empty] | 58.9
|  | 2 | [8 empty] | 58.9
|  | 2 | [8 empty] | 58.9
|  | 2 | [8 empty] | 58.9
|  | 2 | [8 empty] | 58.9
|  | 2 | [8 empty] | 58.9
[5 empty] | Req. MW Load Shed for Block #2 | [7 empty] | Block #2 Total MW Load Shed
[5 empty] | Req. % Load Shed for Block #2 | [7 empty] | Block #2 % Load Shed
Note:
|  | 3 | [8 empty] | 58.7
|  | 3 | [8 empty] | 58.7
|  | 3 | [8 empty] | 58.7
|  | 3 | [8 empty] | 58.7
|  | 3 | [8 empty] | 58.7
[5 empty] | Req. MW Load Shed for Block #3 | [7 empty] | Block #3 Total MW Load Shed
[5 empty] | Req. % Load Shed for Block #3 | [7 empty] | Block #3 % Load Shed
Note:
|  | 4 | [8 empty] | 58.5
|  | 4 | [8 empty] | 58.5
|  | 4 | [8 empty] | 58.5
|  | 4 | [8 empty] | 58.5
|  | 4 | [8 empty] | 58.5
[5 empty] | Req. MW Load Shed for Block #4 | [7 empty] | Block #4 Total MW Load Shed
[5 empty] | Req. % Load Shed for Block #4 | [7 empty] | Block #4 % Load Shed
Note:
|  | 5 | [8 empty] | 58.3
|  | 5 | [8 empty] | 58.3
|  | 5 | [8 empty] | 58.3
|  | 5 | [8 empty] | 58.3
|  | 5 | [8 empty] | 58.3
[5 empty] | Req. MW Load Shed for Block #5 | [7 empty] | Block #5 Total MW Load Shed
[5 empty] | Req. % Load Shed for Block #5 | [7 empty] | Block #5 % Load Shed
Note:
|  | AIES security 1 | [8 empty] | 58.1
|  | AIES security 1 | [8 empty] | 58.1
|  | AIES security 1 | [8 empty] | 58.1
|  | AIES security 1 | [8 empty] | 58.1
|  | AIES security 1 | [8 empty] | 58.1
[5 empty] | Req. MW Load Shed for AIES security 1 | [7 empty] | AIES security 1 Total MW Load Shed
[5 empty] | Req. % Load Shed for AIES security 1 | [7 empty] | AIES security 1 % Load Shed
Note:
|  | AIES security 2 | [8 empty] | 58
|  | AIES security 2 | [8 empty] | 58
|  | AIES security 2 | [8 empty] | 58
|  | AIES security 2 | [8 empty] | 58
|  | AIES security 2 | [8 empty] | 58
[5 empty] | Req. MW Load Shed for AIES security 2 | [7 empty] | AIES security 2 Total MW Load Shed
[5 empty] | Req. % Load Shed for AIES security 2 | [7 empty] | AIES security 2 % Load Shed
Note:
(Page 1 of 3)
UNDER FREQUENCY LOAD SHED
UFLS SCHEDULE (Year) _________
|  | UF Block # | Substation (Element Tripped) | Breaker Number(s) | Substation Name or Line From |  | Line To |  | WECC Zone | WECC Area | Trip Freq. (Hz) | Reset Freq. (Hz) | Trip Time Delay (sec) | Breaker Time (cycles) | Total Tripping Time | Manual Restore Delay Time (Min) | Load Shed MW
[5 empty] | WECC Bus Name | WECC Bus # | WECC Bus Name | WECC Bus #
|  | D1 | [8 empty] | 59.3
|  | D1 | [8 empty] | 59.3
|  | D1 | [8 empty] | 59.3
|  | D1 | [8 empty] | 59.3
|  | D1 | [8 empty] | 59.3
[5 empty] | Req. MW Load Shed for D1 | [7 empty] | D1 Total MW Load Shed
[5 empty] | Req. % Load Shed for D1 | [7 empty] | D1 % Load Shed
Note:
|  | D2 | [8 empty] | 59.5
|  | D2 | [8 empty] | 59.5
|  | D2 | [8 empty] | 59.5
|  | D2 | [8 empty] | 59.5
|  | D2 | [8 empty] | 59.5
|  | D2 | [8 empty] | 59.5
[5 empty] | Req. MW Load Shed for D2 | [7 empty] | D2 Total MW Load Shed
[5 empty] | Req. % Load Shed for D2 | [7 empty] | D2 % Load Shed
Note:
|  | D3 | [8 empty] | 59.5
|  | D3 | [8 empty] | 59.5
|  | D3 | [8 empty] | 59.5
|  | D3 | [8 empty] | 59.5
|  | D3 | [8 empty] | 59.5
|  | D3 | [8 empty] | 59.5
[5 empty] | Req. MW Load Shed for D3 | [7 empty] | D3 Total MW Load Shed
[5 empty] | Req. % Load Shed for D3 | [7 empty] | D3 % Load Shed
Note:
(Page 2 of 3)
UNDER FREQUENCY LOAD SHED
UFLS SCHEDULE (Year) _________
Load automatically restored to correct for frequency overshoot.
|  | Auto Reset Block # | Substation (Element Tripped) | Breaker Number(s) | Substation Name or Line From |  | Line To |  | WECC Zone | WECC Area | Over Freq. (Hz) | Reset Freq. (Hz) | Automatic Restoration Time Delay (sec) |  |  |  | Load Restore MW
[5 empty] | WECC Bus Name | WECC Bus # | WECC Bus Name | WECC Bus #
|  | AR1 | [8 empty] | 60.5
|  | AR1 | [8 empty] | 60.5
[5 empty] | Req. MW Load Restore for AR1 | [7 empty] | Total MW Load Restore
[5 empty] | Req. % Load Restore for AR1 | [7 empty] | % Load Restore for this Block
Note:
|  | AR2 | [8 empty] | 60.7
|  | AR2 | [8 empty] | 60.7
|  | AR2 | [8 empty] | 60.7
[5 empty] | Req. MW Load Restore for AR2 | [7 empty] | Total MW Load Restore
[5 empty] | Req. % Load Restore for AR2 | [7 empty] | % Load Restore for this Block
Note:
|  | AR3 | [8 empty] | 60.9
|  | AR3 | [8 empty] | 60.9
|  | AR3 | [8 empty] | 60.9
[5 empty] | Req. MW Load Restore for AR3 | [7 empty] | Total MW Load Restore
[5 empty] | Req. % Load Restore for AR3 | [7 empty] | % Load Restore for this Block
Note:
Does your company use only solid state and/or microprocessor underfrequency relays to comply with the Alberta Underfrequency Load Shed Program? ____ Yes ____ No
If No, please explain here:
Will your company's frequency relays use define time characteristics and operate within any voltage above 80% of nominal? ____ Yes ____ No
If No, please explain here:
Are there any other exceptions to the Alberta Underfrequency Load Shed Program? ____ Yes ____ No
If Yes, please explain here:
(Page 3 of 3)

## Tab 2a - Detail Load (SL)
use same format with Tab 2, but for System Light

## Revision History
# | Tasks/Actions | Date | Comments
1 | Initial Release | 2021-12-22 | This form is based on the PRC-006-WECC-CRT-3 Attachment A Reporting Form, and revised for PRC-006-AB-3 and the Uderfrequency Load Shed program in Alberta.
2 | Updated | 2025-02-12 | removed columns S and T from Tab 2