## DYR
DYR Data Check
Parameter Group | Parameters | Check | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 5
Dynamic model performance test report |  | Results of the tests listed below must be documented in a report.
Report shall be authenticated and stamped by a professional engineer.
Report shall include the project name, date and revision.
Supporting converted case and SNP file shall be submitted.
Note1: For the dynamic model performance tests below. If the study plant is an energy storage facility (e.g., BESS), the test shall be performed under both charging and discharging operating conditions.
Note2: simulation time step= 1/4 cycle
Note3: Testing scenario shall be designed such that the facility operates at the MARP/MDCP (and/or MACP for BESS charging) for the tests below unless specified.
Note4: For DER project, study case shall include up to the high voltage side of the substation transformer.
Note5: Inifinite bus voltage shall be set to the nominal voltage specific to the service area
Note6: (IBR only) Detail of the tests and acceptance criteria can be found in "2010-001R Facility Modelling Data and List of Electrical and Physical Parameters for Transmission System Model"
Note7: Reference document includes: - AESO Connection Requirements for Inverter-Based Resources (February 2024) - ID# 2010-001R Facility Modelling Data and List of Electrical and Physical Parameters for Transmission System Model - ID# 2017-013R Model Validation and Reactive Power Reporting Guidance - Section 503.4 Voltage Regulation - Section 503.5 Voltage Ride Through - Section 503.6 Frequency and Speed Governing - AESO DER Roadmap Integration Paper - DER Ride-Through Performance Recommendations
Flat start test | This test consists of a minimum 25 second simulation without any disturbance applied and shall be performed with facility operating under the following power dispatch scenarios: - MARP (Pmax) - minimum continuous active power (Pmin) | The test is considered successful if the model initializes correctly without revealing any continuous oscillation or divergence from initial system conditions. Voltage, frequency, and active and reactive power remain almost constant all through the simulation run. | √ | √ | √ | √ | √
Voltage step up and step down tests | The model shall be subject to a 3% voltage step change (in both directions) at the POC. | Transmission connected facility Stage 1 to 3: 1. The test is considered passed if the plant adjusts the reactive power output in an attempt to regulate the POC voltage at the set point. 2. The plant output power should be sustained throughout the small voltage disturbance tests. The unit shall not trip and the response shall be stable. Stage 5: In addition to the acceptance criteria above, the machines shall also comply to the followings: 3. The change in reactive power will achieve 95% of its final value no sooner than 0.1 seconds and no later than one second following a step change in voltage as per Section 503.4 Voltage Regulation 4. (IBR only) The overall dynamic response shall follow Section 6 of "AESO Connection Requirements for Inverter-Based Resources". DER facility 1. The plant output active and reactive power should be sustained throughout the small voltage disturbance tests (assuming constant power factor control mode is used unless specified). The unit shall not trip and the response shall be stable. | √ | √ | √ | √ | √
Frequency step up and step down test | The model shall be subject to a 0.3 Hz step change (in both directions) of system frequency from nominal frequency. The real power output of the plant shall be initially set to 80% of maximum power leaving adequate headroom for the plant to respond to frequency changes. | Transmission connected facility Stage 1 to 3: 1. The plant shall lower or raise its output power in response to the frequency change in accordance with its set droop and frequency dead band characteristics. The unit shall not trip and the response shall be stable. Stage 5: 2. The plant shall lower or raise its output power in response to the frequency change in accordance with its set droop setting. Governor systems can have a deadband up to +/- 0.036Hz. If the frequency is within deadband, no response is required. 3. (IBR only) The overall dynamic response shall follow Table 2 of "AESO Connection Requirements for Inverter-Based Resources". DER facility 1. (Stage 1-5) The plant output active and reactive power can be sustained throughout the small freuqency disturbance tests. The unit shall not trip. Application for IBR if frequency droop is enabled 2. (Applicable to IBR with frequency droop enabled, Stage 1-3) The plant shall lower or raise its output power in response to the frequency change in accordance with its set droop and frequency dead band characteristics. The unit shall not trip and the response shall be stable. If frequency droop settings are enabled in the dynamic model, please provide confirmation from the MP that frequency droop will be implemented. 3. (Application to IBR with frequency droop enabled, Stage 5) The plant shall lower or raise its output power in response to the frequency change in accordance with its set droop and frequency dead band characteristics. Response time (Tresponse) shall meet the requirement in the "DER Ride-Through Performance Recommendations". | √ | √ | √ | √ | √
HVRT | The voltage at POC is varied over time according to high voltage ride through values specified in the followings: 1. IBR: Table 3 of "AESO Connection Requirements for Inverter-Based Resources" 2. Conventional machine: Section 503.5 Voltage Ride Through (if protection model is available) If different voltage ride through requirements are specified in the AESO’s functional specification, those shall be used for this test instead. | Transmission connected facility 1. The test is accepted if the plant successfully runs through the excursion and no protection trips the plant. The plant might operate in ride-through control modes temporarily, during, or right after the disturbance, which might lead to plant real and reactive power output adjustments. However, it is expected the plant returns to pre-disturbance condition once the disturbance is over. 2. For high voltage transient, the model should absorb reactive power throughout the high voltage transient starting immediately or shortly after high voltage transient inception. For 1.1 pu sustained voltage at POC voltage, the plant should provide voltage support to its maximum reactive power capability. The real power should be sustained all through the high voltage transient. However, it might be acceptable to have a modest real power reduction (not more than 5% of plant Pmax) during the transient to accommodate more reactive power absorption. DER facility Not Applicable | √ | √ | √ | √ | √
LVRT | The voltage at POC is varied over time according to high voltage ride through values specified in the followings: 1. IBR: Table 3 of "AESO Connection Requirements for Inverter-Based Resources" 2. Conventional machine: Section 503.5 Voltage Ride Through (if protection model is available) If different voltage ride through requirements are specified in the AESO’s functional specification, those shall be used for this test instead. | Transmission connected facility This test is considered acceptable if the plant successfully runs through the excursion and no protection trips the plant. The plant might operate in ride-through control modes temporarily during or right after the disturbance which might lead to plant real and reactive power output adjustments. However, it is expected the plant returns to at least 90% pre-disturbance condition once the disturbance is over. For low voltage transient, the model should inject reactive current throughout the voltage recovery period. This reactive current injection should happen immediately or shortly after voltage begins to ramp up from zero. Current blocking mode (Momentary Cessation) might be allowed when voltage at POC goes below 0.1 pu. However, the plant shall restart current exchange in less than or equal to five cycles as soon as the voltage goes beyond 0.1 pu. For 0.9 pu sustained voltage at POC voltage, the plant should provide voltage support to its maximum reactive power capability while real power recovers to the full power within 1.0 seconds of POC voltage recovery to 0.9 pu. DER facility Not Applicable | √ | √ | √ | √ | √
LFRT | The frequnecy at POC is varied over time according to the low frequency ride through values specified in the followings: 1. IBR: Figure 7 of "AESO Connection Requirements for Inverter-Based Resources" 2. Conventional machine: Section 503.6 Frequency and Speed Governing (if protection model is available) The grid frequency at POC is ramped up or down at a rate of 5.0 Hz/s.If different frequency ride through requirements are specified in the AESO’s functional specification, those shall be used for this test instead. | Transmission connected facility This test is considered acceptable if the plant successfully runs through the frequency excursion in a stable manner and no protective function trips the plant. The plant might operate in ride-through control modes temporarily during or right after the disturbance which might lead to plant real and reactive power output adjustments. However, it is expected the plant returns to the pre-disturbance condition once the disturbance is over. DER facility Not Applicable | √ | √ | √ | √ | √
HFRT | The frequnecy at POC is varied over time according to the low frequency ride through values specified in the followings: 1. IBR: Figure 7 of "AESO Connection Requirements for Inverter-Based Resources" 2. Conventional machine: Section 503.6 Frequency and Speed Governing (if protection model is available) The grid frequency at POC is ramped up or down at a rate of 5.0 Hz/s.If different frequency ride through requirements are specified in the AESO’s functional specification, those shall be used for this test instead. | Transmission connected facility This test is considered acceptable if the plant successfully runs through the frequency excursion in a stable manner and no protective function trips the plant. The plant might operate in ride-through control modes temporarily during or right after the disturbance which might lead to plant real and reactive power output adjustments. However, it is expected the plant returns to pre-disturbance condition once the disturbance is over. DER facility Not Applicable | √ | √ | √ | √ | √
SCR | The model shall be tested for the minimum SCL value specified by the AESO, or when the SCL corresponds to SCR = 3.0, whichever is lower, at POC starting from a strong system condition toward weaker conditions. The SCR adjustment is achieved by varying the Thevenin circuit impedance. The simulation starts at a pre-defined SCR followed by applying a solid three phase to ground fault at POC which will be cleared after 6 cycles. | Transmission connected facility 1. For IBRs, models should provide a stable or well-damped oscillatory response for the minimum SCR specified by the AESO or SCR=3 (whichever is lower). The plant reactive power output shall reflect a proper action by plant AVR. This means the plant AVR should respond to restore voltage schedule at POC by adjusting of plant reactive power output. 2. This test is not applicable to transmission connected conventional machines. DER facility Not Applicable | √ | √ | √ | √ | √
Fault recovery | Thevenin circuit impedance is determined at the POC using the latest OPBC and used in the test. The model performance shall be tested when the facility is subject to faults at POC. 3-phase to ground fault with 6-cycle clearing time applied at the POC bus shall be performed. | Models shall provide a stable or well damped oscillatory response following and during fault recovery time. | √ | √ | √ | √ | √
Reference setpoint step test | Thevenin circuit impedance is determined at the POC using the latest OPBC and used in the test. The model shall be subject to a 5% step changes on the following reference setpoint in power plant controller. • Voltage reference • Frequency reference | Transmission connected facility 1. For IBRs, this test is considered acceptable if the plant follows the reference set point and settles within a reasonable time. The overall dynamic response shall follow "ID 2010-001R Facility Modelling Data and List of Electrical and Physical Parameters for Transmission System Model". 2. This test is not applicable to transmission connected conventional machines. DER facility Not Applicable |  |  |  |  | √
PSSE results should benchmark with EMT results (for both transmission and distribution connected power electronic based facilities as per ID#2010-001R) | [6 empty] | √