## Information
This analysis tool is not authoritative and is for information purposes only and intended to provide guidance and information to the AESO. In the event of any discrepancy between this tool and any authoritative document1 in effect, the authoritative document governs.
1 Purpose
This analysis tool is intended to allow the AESO to assess a Rate DOS, Demand Opportunity Service, applicant's anticipated load characteristics and determine eligibility for Rate DOS.
The calculations in this analysis tool estimates revenues for Rate DOS and Rate DTS, Demand Transmission Service, based on currently approved ISO tariff rates (2024 ISO tariff).
2 Completing the Anticipated Rate DOS Load Characteristics tool
This section describes how a market participant may complete the analysis tool to provide information to the AESO to determine Rate DOS eligibility and assist the Market Participant in preparing their Evidence of Eligibility.
Initial Steps
Select appropriate tab to input load characteristics - "With no Rate DTS Reduction" if no Rate DTS decrease is
being applied for and "With Rate DTS Reduction" if a Rate DTS reduction is being applied for in combination with
an application for new or increased Rate DOS contract.
The information included in both tabs will allow revenue calculations under 2 or 3 scenarios based on the requirement for a Rate DTS reduction or not.
Adjusting Input Data
All yellow shaded fields in the analysis tabs should be filled in or adjusted.
Results
The analysis of the outputs by the AESO will involve assessing the revenue impact across the 2 or 3 different scenarios to determine if Rate DOS will result in additional revenue collected from the ISO tariff.
For assistance with Schedule B, please contact the AESO at: |  | dos.operations@aeso.ca
Attachments
With no Rate DTS Reduction - Rate DOS Eligibility Analysis with no Rate DTS reduction
With Rate DTS Reduction - Rate DOS Eligibility Analysis with Rate DTS reduction
Revision History
Date | Description
2025-02-01 | Initial Release.
1 “Authoritative document” is the general name given by the AESO to categories of documents made by the AESO
under the authority of the Electric Utilities Act and associated regulations, and that contain binding legal requirements for
either market participants or the AESO, or both. Authoritative documents include: the ISO rules, the reliability standards
and the ISO tariff.
Schedule B
Load Characteristics

## No Rate DTS Reduction
Alberta Electric System Operator | [13 empty] | With no Rate DTS Reduction - Rate DOS Eligibility Analysis with no Rate DTS reduction
Proposed Rate DOS, Demand Opportunity Service, of the ISO tariff
Schedule A - Load Characteristics [Assessment of proposed Rate DTS and Rate DOS load characteristics]
With No Accompanying Rate DTS Reduction
Date: |  | 2024-03-12
Market Participant Name: |  | Market Participant A
Project Number / Site Name |  | Testing Site 1
Site Sample 3
Scenario |  | Rate DTS Contract Capacity (MW) | Rate PSC Applicable | Rate DOS Contract Capacity (MW) | Rate STS Contract Capacity (MW) | Substation Fraction | Total Load Factor (%) | Rate DTS Load Factor (%) | Annual Average Pool Price | Site Realized Annual Average Pool Price | DOS Loss Factor (%) | Average Coincident Peak (MW) | Coincidence Factor (%) | Annual Energy (MWh)
Scenario 1 | Rate DTS Only | 5 | Yes |  | 50 | 0.090909 | 20% | 20% | 80 | 30 |  | 1 | 20% | 8760 | Testing Site 1 - Estimated Annual Transmission Revenue
Scenario 2 | with Rate DTS and Rate DOS - Dispatchable | 5 | Yes | 45 | 50 | 0.090909 | 20% | 80% | 80 | 30 | 2% | 1 | 20% | 87600
Estimated Transmission Costs | [13 empty] | Total Bill with Energy Settlement
Scenario |  | Rate DTS Contract Capacity (MW) | Rate DOS Contract Capacity (MW) | Average Coincident Peak (MW) | Coincidence Factor (%) | Annual Energy (MWh) | Total Load Factor (%) | Rate DTS ($) | Rate DOS - Dispatchable ($) | Potential Rate DTS Revenue Loss (Gain) ($) | Total Transmission Costs ($) | Average Transmission Cost ($/MWh) | Additional Transmission Revenue (%) | Site Realized Energy Costs ($) | Total ISO Tariff Bill ($) | Estimated Impact (%)
Scenario 1 - Rate DTS Only |  | 5 | n/a | 1 | 20% | 8760 | 20% | 371052.7527 | n/a | n/a | 371052.7527 | 42.3576 | -- | 262800 | 633852.7527 | -- | Testing Site 1 - Annual Energy Consumption and Average Transmission Charge $/MWh
Scenario 2 - with Rate DTS and Rate DOS - Dispatchable |  | 5 | 45 | 1 | 20% | 87600 | 20% | 371052.7527 | 784300.32 | n/a | 1155353.0727 | 13.189 | 211.4% | 2628000 | 3783353.0727 | 496.9%
[Scenario 2] - Charged as Rate DTS Only |  | 50 | n/a | 0 | 0% | 87600 | 20% | 1155353.0727 | n/a | 1121567.7273 | 2276920.8 | 25.9922 | 97.08% | 2628000 | 4904920.8 | 29.64%
Note on M36: Author: Values of these cells can be used in Schedule A to illustrate relative cost of electric energy
Note on F37: Author: Estimation of CF if all energy (in Scenario B) consumed under Rate DTS

## With Rate DTS Reduction
Alberta Electric System Operator | [13 empty] | With Rate DTS Reduction - Rate DOS Eligibility Analysis with Rate DTS reduction
Proposed Rate DOS, Demand Opportunity Service, of the ISO tariff
Assessment of proposed Rate DTS and Rate DOS load characteristics
With An Accompanying Rate DTS Reduction
Date: |  | 2024-03-12
Market Participant Name: |  | Market Participant B
Project Number / Site Name |  | Testing Site 2
Site Sample 3
Scenario |  | Rate DTS Contract Capacity (MW) | Rate PSC Applicable | Rate DOS Contract Capacity (MW) | Rate STS Contract Capacity (MW) | Substation Fraction | Total Load Factor (%) | Rate DTS Load Factor (%) | Annual Average Pool Price | Site Realized Annual Average Pool Price | DOS Loss Factor (%) | Average Coincident Peak (MW) | Coincidence Factor (%) | Annual Energy (MWh)
Scenario 1 | Rate DTS Only (Existing Load Profile) | 120 | No |  | 0 | 1 | 72% | 72% | 80 | 30 |  | 2.4 | 2% | 756864 | Testing Site 2 - Estimated Annual Transmission Revenue
Scenario 2 | with Rate DTS and Rate DOS - Dispatchable | 10 | No | 110 | 0 | 1 | 90% | 70% | 80 | 30 | 2% | 5 | 50% | 946080
Estimated Transmission Costs | [13 empty] | Total Bill with Energy Settlement
Rate |  | Rate DTS Contract Capacity (MW) | Rate DOS Contract Capacity (MW) | Average Coincident Peak (MW) | Coincidence Factor (%) | Annual Energy (MWh) | Total Load Factor (%) | Rate DTS ($) | Rate DOS - Dispatchable ($) | Potential Rate DTS Revenue Loss (Gain) ($) | Total Transmission Costs ($) | Average Transmission Cost ($/MWh) | Additional Transmission Revenue (%) | Site Realized Energy Costs ($) | Total ISO Tariff Bill ($) | Estimated Impact (%)
Scenario 1 - Rate DTS Only (Existing Load Profile) |  | 120 | n/a | 2.4 | 2% | 756864 | 72% | 10421502.672 | n/a | n/a | 10421502.672 | 13.7693 | -- | 22705920 | 33127422.672 | --
Scenario 2 - with Rate DTS and Rate DOS - Dispatchable |  | 10 | 110 | 5 | 50% | 946080 | 90% | 1967460.36 | 8801592.48 | 0 | 10769052.84 | 11.3828 | 3.335% | 28382400 | 39151452.84 | 18.18%
Additional Transmission Revenue with DOS Dispatchable* | [7 empty] | 10421502.672 |  | 347550.168 |  |  | 3.335%
[Scenario 2] - Charged as Rate DTS Only |  |  |  |  | 30% | 946080 |  | 10769052.84 |  | 4883829 | 15652881.84 | 16.545 | 50.2% | 28382400 | 44035281.84 | 12.47%
Note on F39: Author: Estimation of CF if all energy (in Scenario B) consumed under Rate DTS
Note on M39: Author: Values of these cells can be used in Schedule A to illustrate relative cost of electric energy

## No Rate DTS Reduction Calcs (hidden)
Date: |  | 2024-11-20 | [8 empty] | Estimated Total Bill Impact |  |  |  | 496.9% | Estimated Total Bill Impact |  |  |  | 29.64%
[11 empty] | Estimated Transmission Costs Impact |  |  |  | 211.4% | Estimated Transmission Costs Impact |  |  |  | 97.08%
[8 empty] | Tariff Year | 2024 |  |  |  |  | Tariff: | Rate DOS |  |  |  | Tariff: | Rate DTS
[6 empty] | Scenario 1 |  |  |  |  | Scenario 2 |  |  |  |  | Assessment
|  |  |  | Scenario A |  | Rate DTS Only |  |  |  | Scenario A | With Rate DTS and Rate DOS - Dispatchable |  |  |  |  | [B] Consumption - Rate DTS Only
| Rate DTS - Billing Determinants |  |  |  | Factor | Monthly Average | Annual Volumes |  |  |  | Factor | Monthly Average | Annual Volumes |  |  | Factor | Monthly Average | Annual Volumes
| (a) | Substation fraction (SF) |  |  |  |  | 0.090909 | [5 empty] | 0.090909 |  |  |  |  | 0.5
| (b) | Rate PSC Applicable |  |  |  |  | Yes | [5 empty] | Yes |  |  |  |  | Yes
| (c) | Highest metered demand |  |  |  | 5 | 60 | MW |  |  |  | 5 | 60 | MW |  |  | 50 | 600 | MW
| (d) | Coincident metered demand |  |  | 20% | 1 | 12 | MW |  |  | 20% | 1 | 12 | MW |  | 0% | 0 | 0 | MW
| (e) | Contract Capacity |  |  |  | 5 | 5 | MW |  |  |  | 5 | 60 | MW |  |  | 50 | 600 | MW
| (f) | Metered energy |  |  | 20% | 730 | 8760 | MWh |  |  | 80% |  | 8760 | MWh |  | 20% |  | 87600 | MWh
| (g) | Billing capacity |  |  |  | 5 | 60 | MW |  |  |  | 5 | 60 | MW |  |  |  | 600 | MW
| (i) | Apparent power factor difference |  |  |  |  | 0 | MVA |  |  |  |  | 0 | MVA |  |  |  | 0 | MVA
| (k) | Site Average Pool Price on Energy Settlement |  |  |  |  | 30 | /MWh |  |  |  |  | 30 | /MWh |  |  |  | 30 | /MWh
| (l) | Annual Average Pool Price |  |  |  |  | 80 | /MWh |  |  |  |  | 80 | /MWh |  |  |  | 80 | /MWh
| (m) | Rate STS |  |  |  | 50 |  | MW |  |  |  | 50 |  | MW |  |  | 50 |  | MW
| Rate DOS - Dispatchable - Billing Determinants |  |  |  | Factor | Monthly Average | Applicable Volumes |  |  |  | Factor | Monthly Average | Applicable Volumes
| (a) | Contract Capacity | [9 empty] | 45 | 540 | MW
| (b) | Metered energy | [10 empty] | 78840 | MWh
| (d) | Site Average Pool Price on Energy Settlement | [10 empty] | 30 | /MWh
| (e) | Annual Average Pool Price | [10 empty] | 80 | /MWh
| (f) | Loss Factor | [8 empty] | 2% |  | 2%
Rate or Rider Component |  |  |  |  | Rate |  | Volume |  | Amount |  | Rate |  | Volume |  | Amount | Rate |  | Volume |  | Amount
Rate DTS: Demand Transmission Service | [10 empty] | Rate DTS: Demand Transmission Service |  |  |  |  | Rate DTS: Demand Transmission Service
Connection Charge
Bulk System Charge
3(a) | Coincident metered demand |  |  |  | 10899 | /MW/month | 12 | MW | 130788 |  | 10899 | /MW/month | 12 | MW | 130788 | 10899 | /MW/month | 0 | MW | 0
3(b) | Bulk - metered energy |  |  |  | 1.22 | /MWh | 8760 | MWh | 10687.2 |  | 1.22 | /MWh | 8760 | MWh | 10687.2 | 1.22 | /MWh | 87600 | MWh | 106872
Regional System Charge
3(b) | Billing capacity |  |  |  | 2841 | /MW/month | 60 | MW | 170460 |  | 2841 | /MW/month | 60 | MW | 170460 | 2841 | /MW/month | 600 | MW | 1704600
3(c) | Metered energy |  |  |  | 0.92 | /MWh | 8760 | MWh | 8059.2 |  | 0.92 | /MWh | 8760 | MWh | 8059.2 | 0.92 | /MWh | 87600 | MWh | 80592
Point of Delivery Charge
3(e) | Substation fraction |  |  |  | 14641 | /month | 0.090909 |  | 15972 |  | 14641 | /month | 0.090909 |  | 15972 | 14641 | /month | 0.5 |  | 87846
3(f) | First (7.5 × SF) MW of billing capacity |  |  |  | 4819 | /MW/month | 0.68182 | MW | 39428.1818 |  | 4819 | /MW/month | 0.68182 | MW | 39428.1818 | 4819 | /MW/month | 3.75 | MW | 216855
3(g) | Next (9.5 × SF) MW of billing capacity |  |  |  | 2858 | /MW/month | 0.86364 | MW | 29619.2727 |  | 2858 | /MW/month | 0.86364 | MW | 29619.2727 | 2858 | /MW/month | 4.75 | MW | 162906
3(h) | Next (23 × SF) MW of billing capacity |  |  |  | 1913 | /MW/month | 2.0909 | MW | 47998.9091 |  | 1913 | /MW/month | 2.0909 | MW | 47998.9091 | 1913 | /MW/month | 11.5 | MW | 263994
3(i) | All remaining MW of billing capacity |  |  |  | 1178 | /MW/month | 1.3636 | MW | 19276.3636 |  | 1178 | /MW/month | 1.3636 | MW | 19276.3636 | 1178 | /MW/month | 30 | MW | 424080
Total Wires | [8 empty] | 472289.1273 |  | Total Wires |  |  |  | 472289.1273 | Total Wires |  |  |  | 3047745
Operating Reserve Charge Estimate
4 | Metered energy |  | pool price | 7.18% | 30 | /MWh | 8760 | MWh | 18869.04 |  | 30 | /MWh | 8760 | MWh | 18869.04 | 30 | /MWh | 87600 | MWh | 188690.4
Transmission Constraint Rebalancing Charge Estimate
5 | Metered energy |  |  |  | 0.069 | /MWh | 8760 | MWh | 604.44 |  | 0.069 | /MWh | 8760 | MWh | 604.44 | 0.069 | /MWh | 87600 | MWh | 6044.4
Voltage Control Charge
6 | Metered energy |  |  |  | 0.06 | /MWh | 8760 | MWh | 525.6 |  | 0.06 | /MWh | 8760 | MWh | 525.6 | 0.06 | /MWh | 87600 | MWh | 5256
Other System Support Services Charge
7(a) | Highest metered demand |  |  |  | 52 | /MW/month | 60 | MW | 3120 |  | 52 | /MW/month | 60 | MW | 3120 | 52 | /MW/month | 600 | MW | 31200
7(b) | Apparent power difference |  |  |  | 400 | /MVA/month | 0 | MVA | 0 |  | 400 | /MVA/month | 0 | MVA | 0 | 400 | /MVA/month | 0 | MVA | 0
Total Rate DTS | [8 empty] | 495408.2073 |  | Total Rate DTS |  |  |  | 495408.2073 | Total Rate DTS |  |  |  | 3278935.8
Rate Primary Service Credit
| Substation fraction |  |  |  | -11566 | /month | 0.090909 |  | -12617.4545 |  | -11566 | /month | 0.090909 |  | -12617.4545 | -11566 | /month | 0.5 |  | -69396
| First (7.5 × SF) MW of billing capacity |  |  |  | -3807 | /MW/month | 0.68182 | MWh | -31148.1818 |  | -3807 | /MW/month | 0.68182 | MWh | -31148.1818 | -3807 | /MW/month | 3.75 | MWh | -171315
| Next (9.5 × SF) MW of billing capacity |  |  |  | -2258 | /MW/month | 0.86364 | MWh | -23401.0909 |  | -2258 | /MW/month | 0.86364 | MWh | -23401.0909 | -2258 | /MW/month | 4.75 | MWh | -128706
| Next (23 × SF) MW of billing capacity |  |  |  | -1511 | /MW/month | 2.0909 | MWh | -37912.3636 |  | -1511 | /MW/month | 2.0909 | MWh | -37912.3636 | -1511 | /MW/month | 11.5 | MWh | -208518
| All remaining MW of billing capacity |  |  |  | -1178 | /MW/month | 1.3636 | MWh | -19276.3636 |  | -1178 | /MW/month | 1.3636 | MWh | -19276.3636 | -1178 | /MW/month | 30 | MWh | -424080
Total Rate PSC Credit | [8 empty] | -124355.4545 |  | Total Rate PSC Credit |  |  |  | -124355.4545 | Total Rate PSC Credit |  |  |  | -1002015
Total Rate DTS and Rate PSC | [8 empty] | 371052.7527 |  | Total Rate DTS and Rate PSC |  |  |  | 371052.7527 | Total Rate DTS and Rate PSC |  |  |  | 2276920.8
[11 empty] | Rate |  | Volume |  | Amount
Updated Rate DOS: Demand Opportunity Service
Bulk System Charge
| Fixed | [9 empty] | 3.472 | /MWh | 78840 | MWh | 273732.48
| Usage | [9 empty] | 1.22 | /MWh | 78840 | MWh | 96184.8
Regional System Charge
| Fixed | [9 empty] | 1.582 | /MWh | 78840 | MWh | 124724.88
| Usage | [9 empty] | 0.92 | /MWh | 78840 | MWh | 72532.8
[11 empty] | Total Wires |  |  |  | 567174.96
Operating Reserve Charge Estimate
4 | Metered energy |  | pool price | 7.18% | [6 empty] | 30 | /MWh | 78840 | MWh | 169821.36
Transmission Constraint Rebalancing Charge Estimate
5 | Metered energy
Voltage Control Charge
6 | Metered energy
Other System Support Services Charge
7(a) | Highest metered demand
Losses Charge
4 | Metered energy |  | pool price | 2% | [6 empty] | 30 | /MWh | 78840 | MWh | 47304
[11 empty] | Total Rate DOS |  |  |  | 784300.32
Transmission Costs | [8 empty] | 371052.7527 |  | Transmission Costs |  |  |  | 1155353.0727 | Transmission Costs |  |  |  | 2276920.8
[11 empty] | Transmission Costs Impact |  |  |  | 211.4% | Transmission Costs Impact |  |  |  | 97.08%
Energy Market Settlement |  |  |  |  | 30 | /MWh | 8760 | MWh | 262800 |  | Energy Market Settlement |  | 87600 | MWh | 2628000 | Energy Market Settlement |  | 87600 | MWh | 2628000
Total Bill | [8 empty] | 633852.7527 |  | Total Bill |  |  |  | 3783353.0727 | Total Bill |  |  |  | 4904920.8
[11 empty] | Total Bill Impact |  |  |  | 496.9% | Total Bill Impact |  |  |  | 29.64%
[11 empty] | Total Additional Revenue |  |  |  | 784300.32 | Revenue Reduction of Same Load - Rate DTS vs Rate DTS + Rate DOS |  |  |  | -1121567.7273
[11 empty] | Additional Revenue on Bulk charges |  |  |  | 369917.28 | Additional Revenue on Bulk charges |  |  |  | 404520.48
[11 empty] | Additional Revenue on Regional charges |  |  |  | 197257.68 | Additional Revenue on Regional charges |  |  |  | -1409415.12
[11 empty] | Additional Revenue on POD charges only |  |  |  | 0 | Additional Revenue on POD charges only |  |  |  | -125726.7273
[11 empty] | Additional Revenue on other charges |  |  |  | 217125.36 | Additional Revenue on other charges |  |  |  | 9053.64
[15 empty] | 784300.32 |  |  |  |  | -1121567.7273
Note on G10: Author: Load pattern if only rate available was Rate DTS.
Note on L10: Author: Load pattern if Rate DOS was applicable/available
Note on R10: Author: Keeping load consumption same as if Rate DOS, was applicable, what would Rate DTS result in

## Rate DTS Reduction Calcs (hidden)
Date: |  | 2024-11-20 | [7 empty] | Estimated Total Bill Impact |  |  |  | 18.18% | Estimated Total Bill Impact |  |  |  | 12.47%
[10 empty] | Estimated Transmission Costs Impact |  |  |  | 3.335% | Estimated Transmission Costs Impact |  |  |  | 45.35%
[8 empty] | Tariff Year | 2024 |  |  |  | Tariff: | Rate DOS |  |  |  | Tariff: | Rate DTS
[6 empty] | Scenario 1 |  |  |  | Scenario 2 |  |  |  |  | Assessment
|  |  |  | Scenario A |  | Rate DTS Only (Existing Load Profile) |  |  |  | With Rate DTS and Rate DOS - Dispatchable |  |  |  |  | [B] Consumption - Rate DTS Only
| Rate DTS - Billing Determinants |  |  |  | Factor | Monthly Average | Annual Volumes |  |  | Factor | Monthly Average | Annual Volumes |  |  | Factor | Monthly Average | Annual Volumes
| (a) | Substation fraction (SF) |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 1
| (b) | Rate PSC Applicable |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No
| (c) | Highest metered demand |  |  |  | 120 | 1440 | MW |  |  | 10 | 120 | MW |  |  | 120 | 1440 | MW
| (d) | Coincident metered demand |  |  | 2% | 2.4 | 28.8 | MW |  |  | 5 | 60 | MW |  | 30% | 36 | 432 | MW
| (e) | Contract Capacity |  |  |  | 120 | 120 | MW |  |  | 10 | 120 | MW |  |  | 120 | 1440 | MW
| (f) | Metered energy |  |  | 72% | 63072 | 756864 | MWh |  | 70% |  | 61320 | MWh |  | 0% |  | 946080 | MWh
| (g) | Billing capacity |  |  |  | 120 | 1440 | MW |  |  |  | 120 | MW |  |  |  | 1440 | MW
| (i) | Apparent power factor difference |  |  |  |  | 0 | MVA |  |  |  | 0 | MVA |  |  |  | 0 | MVA
| (k) | Site Average Pool Price on Energy Settlement |  |  |  |  | 30 | /MWh |  |  |  | 30 | /MWh |  |  |  | 30 | /MWh
| (l) | Annual Average Pool Price |  |  |  |  | 80 | /MWh |  |  |  | 80 | /MWh |  |  |  | 80 | /MWh
| (m) | Rate STS |  |  |  | 0 |  | MW |  |  | 0 |  | MW |  |  | 0 |  | MW
| Rate DOS - Dispatchable - Billing Determinants |  |  |  | Factor | Monthly Average | Applicable Volumes |  |  | Factor | Monthly Average | Applicable Volumes
| (a) | Contract Capacity | [8 empty] | 110 | 1320 | MW
| (b) | Metered energy | [9 empty] | 884760 | MWh
| (d) | Site Average Pool Price on Energy Settlement | [9 empty] | 30 | /MWh
| (e) | Annual Average Pool Price | [9 empty] | 80 | /MWh
| (f) | Loss Factor | [7 empty] | 2% |  | 2%
Rate or Rider Component |  |  |  |  | Rate |  | Volume |  | Amount | Rate |  | Volume |  | Amount | Rate |  | Volume |  | Amount
Rate DTS: Demand Transmission Service | [9 empty] | Rate DTS: Demand Transmission Service |  |  |  |  | Rate DTS: Demand Transmission Service
Connection Charge
Bulk System Charge
3(a) | Coincident metered demand |  |  |  | 10899 | /MW/month | 28.8 | MW | 313891.2 | 10899 | /MW/month | 60 | MW | 653940 | 10899 | /MW/month | 432 | MW | 4708368
3(b) | Bulk - metered energy |  |  |  | 1.22 | /MWh | 756864 | MWh | 923374.08 | 1.22 | /MWh | 61320 | MWh | 74810.4 | 1.22 | /MWh | 946080 | MWh | 1154217.6
Regional System Charge
3(b) | Billing capacity |  |  |  | 2841 | /MW/month | 1440 | MW | 4091040 | 2841 | /MW/month | 120 | MW | 340920 | 2841 | /MW/month | 1440 | MW | 4091040
3(c) | Metered energy |  |  |  | 0.92 | /MWh | 756864 | MWh | 696314.88 | 0.92 | /MWh | 61320 | MWh | 56414.4 | 0.92 | /MWh | 946080 | MWh | 870393.6
Point of Delivery Charge
3(e) | Substation fraction |  |  |  | 14641 | /month | 1 |  | 175692 | 14641 | /month | 1 |  | 175692 | 14641 | /month | 1 |  | 175692
3(f) | First (7.5 × SF) MW of billing capacity |  |  |  | 4819 | /MW/month | 7.5 | MW | 433710 | 4819 | /MW/month | 7.5 | MW | 433710 | 4819 | /MW/month | 7.5 | MW | 433710
3(g) | Next (9.5 × SF) MW of billing capacity |  |  |  | 2858 | /MW/month | 9.5 | MW | 325812 | 2858 | /MW/month | 2.5 | MW | 85740 | 2858 | /MW/month | 9.5 | MW | 325812
3(h) | Next (23 × SF) MW of billing capacity |  |  |  | 1913 | /MW/month | 23 | MW | 527988 | 1913 | /MW/month | 0 | MW | 0 | 1913 | /MW/month | 23 | MW | 527988
3(i) | All remaining MW of billing capacity |  |  |  | 1178 | /MW/month | 80 | MW | 1130880 | 1178 | /MW/month | 0 | MW | 0 | 1178 | /MW/month | 80 | MW | 1130880
Total Wires | [8 empty] | 8618702.16 | Total Wires |  |  |  | 1821226.8 | Total Wires |  |  |  | 13418101.2
Operating Reserve Charge Estimate
4 | Metered energy |  | pool price | 7.18% | 30 | /MWh | 756864 | MWh | 1630285.056 | 30 | /MWh | 61320 | MWh | 132083.28 | 30 | /MWh | 946080 | MWh | 2037856.32
Transmission Constraint Rebalancing Charge Estimate
5 | Metered energy |  |  |  | 0.069 | /MWh | 756864 | MWh | 52223.616 | 0.069 | /MWh | 61320 | MWh | 4231.08 | 0.069 | /MWh | 946080 | MWh | 65279.52
Voltage Control Charge
6 | Metered energy |  |  |  | 0.06 | /MWh | 756864 | MWh | 45411.84 | 0.06 | /MWh | 61320 | MWh | 3679.2 | 0.06 | /MWh | 946080 | MWh | 56764.8
Other System Support Services Charge
7(a) | Highest metered demand |  |  |  | 52 | /MW/month | 1440 | MW | 74880 | 52 | /MW/month | 120 | MW | 6240 | 52 | /MW/month | 1440 | MW | 74880
7(b) | Apparent power difference |  |  |  | 400 | /MVA/month | 0 | MVA | 0 | 400 | /MVA/month | 0 | MVA | 0 | 400 | /MVA/month | 0 | MVA | 0
Total Rate DTS | [8 empty] | 10421502.672 | Total Rate DTS |  |  |  | 1967460.36 | Total Rate DTS |  |  |  | 15652881.84
Rate Primary Service Credit
| Substation fraction |  |  |  | -11566 | /month | 1 |  | 0 | -11566 | /month | 1 |  | 0 | -11566 | /month | 1 |  | 0
| First (7.5 × SF) MW of billing capacity |  |  |  | -3807 | /MW/month | 7.5 | MWh | 0 | -3807 | /MW/month | 7.5 | MWh | 0 | -3807 | /MW/month | 7.5 | MWh | 0
| Next (9.5 × SF) MW of billing capacity |  |  |  | -2258 | /MW/month | 9.5 | MWh | 0 | -2258 | /MW/month | 2.5 | MWh | 0 | -2258 | /MW/month | 9.5 | MWh | 0
| Next (23 × SF) MW of billing capacity |  |  |  | -1511 | /MW/month | 23 | MWh | 0 | -1511 | /MW/month | 0 | MWh | 0 | -1511 | /MW/month | 23 | MWh | 0
| All remaining MW of billing capacity |  |  |  | -1178 | /MW/month | 80 | MWh | 0 | -1178 | /MW/month | 0 | MWh | 0 | -1178 | /MW/month | 80 | MWh | 0
Total Rate PSC Credit | [8 empty] | 0 | Total Rate PSC Credit |  |  |  | 0 | Total Rate PSC Credit |  |  |  | 0
Total Rate DTS and Rate PSC | [8 empty] | 10421502.672 | Total Rate DTS and Rate PSC |  |  |  | 1967460.36 | Total Rate DTS and Rate PSC |  |  |  | 15652881.84
[10 empty] | Rate |  | Volume |  | Amount
Updated Rate DOS: Demand Opportunity Service
Bulk System Charge
| Fixed | [8 empty] | 3.472 | /MWh | 884760 | MWh | 3071886.72
| Usage | [8 empty] | 1.22 | /MWh | 884760 | MWh | 1079407.2
Regional System Charge
| Fixed | [8 empty] | 1.582 | /MWh | 884760 | MWh | 1399690.32
| Usage | [8 empty] | 0.92 | /MWh | 884760 | MWh | 813979.2
[10 empty] | Total Wires |  |  |  | 6364963.44
Operating Reserve Charge Estimate
4 | Metered energy |  | pool price | 7.18% | [5 empty] | 30 | /MWh | 884760 | MWh | 1905773.04
Transmission Constraint Rebalancing Charge Estimate
5 | Metered energy
Voltage Control Charge
6 | Metered energy
Other System Support Services Charge
7(a) | Highest metered demand
Losses Charge
4 | Metered energy |  | pool price | 2% | [5 empty] | 30 | /MWh | 884760 | MWh | 530856
[10 empty] | Total Rate DOS |  |  |  | 8801592.48
Transmission Costs | [8 empty] | 10421502.672 | Transmission Costs |  |  |  | 10769052.84 | Transmission Costs |  |  |  | 15652881.84
[10 empty] | Transmission Costs Impact |  |  |  | 3.335% | Transmission Costs Impact |  |  |  | 45.35%
Energy Market Settlement |  |  |  |  | 30 | /MWh | 756864 | MWh | 22705920 | Energy Market Settlement |  | 946080 | MWh | 28382400 | Energy Market Settlement |  | 946080 | MWh | 28382400
Total Bill | [8 empty] | 33127422.672 | Total Bill |  |  |  | 39151452.84 | Total Bill |  |  |  | 44035281.84
[10 empty] | Total Bill Impact |  |  |  | 18.18% | Total Bill Impact |  |  |  | 12.47%
[10 empty] | Total Additional Revenue |  |  |  | 347550.168 | Revenue Reduction of Same Load - Rate DTS vs Rate DTS + Rate DOS |  |  |  | -4883829
[10 empty] | Additional Revenue on Bulk charges |  |  |  | 3642779.04 | Additional Revenue on Bulk charges |  |  |  | -982541.28
[10 empty] | Additional Revenue on Regional charges |  |  |  | -2176350.96 | Additional Revenue on Regional charges |  |  |  | -2350429.68
[10 empty] | Additional Revenue on POD charges only |  |  |  | -1898940 | Additional Revenue on POD charges only |  |  |  | -1898940
[10 empty] | Additional Revenue on other charges |  |  |  | 780062.088 | Additional Revenue on other charges |  |  |  | 348081.96
[14 empty] | 347550.168 |  |  |  |  | -4883829
Note on G10: Author: Current l oad pattern if only rate available was Rate DTS.
Note on L10: Author: Load pattern if Rate DOS was applicable/available
Note on R10: Author: Keeping load consumption same as if Rate DOS, was applicable, what would Rate DTS result in

## Rates Lookup (hidden)
| Tariff | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | Rate DOS
| Effective On |  |  |  |  | 2021-01-01 | 2022-01-01 | 2023-01-01 | 2024-01-01
| End Date |  |  |  |  | 2021-12-31 | 2022-12-31 | 2023-12-31 | Current
Bulk System Charge | Coincident metered demand |  |  |  |  | 11085 | 10501 | 10840 | 10899
Bulk System Charge | Metered energy |  |  |  |  | 1.22 | 1.15 | 1.18 | 1.22 | 1.22
Regional System Charge | Billing capacity |  |  |  |  | 2893 | 2775 | 2844 | 2841
Regional System Charge | Metered energy |  |  |  |  | 0.93 | 0.87 | 0.9 | 0.92 | 0.92
Rate DTS Charge | (e) Substation fraction (SF) |  |  |  |  | 14860 | 14332 | 14728 | 14641
Rate DTS Charge | (f) First (7.5 × SF) MW of billing capacity |  |  |  |  | 4891 | 4717 | 4847 | 4819
Rate DTS Charge | (g) Next (9.5 × SF) MW of billing capacity |  |  |  |  | 2900 | 2797 | 2875 | 2858
Rate DTS Charge | (h) Next (23 × SF) MW of billing capacity |  |  |  |  | 1942 | 1873 | 1924 | 1913
Rate DTS Charge | (i) All remaining MW of billing capacity |  |  |  |  | 1195 | 1153 | 1185 | 1178
Rate PSC Credit | (e) Substation fraction (SF) |  |  |  |  | -11739 | -11322 | -11635 | -11566
Rate PSC Credit | (f) First (7.5 × SF) MW of billing capacity |  |  |  |  | -3864 | -3726 | -3829 | -3807
Rate PSC Credit | (g) Next (9.5 × SF) MW of billing capacity |  |  |  |  | -2291 | -2210 | -2271 | -2258
Rate PSC Credit | (h) Next (23 × SF) MW of billing capacity |  |  |  |  | -1534 | -1480 | -1520 | -1511
Rate PSC Credit | (i) All remaining MW of billing capacity |  |  |  |  | -1195 | -1153 | -1185 | -1178
Operating Reserve Charge | Pool price (Actual) |  |  |  |  | 101.93 | 162.46 | 150 | 83.42 | 83.42
Operating Reserve Charge | Multiplier |  |  |  |  | 6.19% | 4.53% | 5.18% | 7.18% | 7.18%
Transmission Constraint Rebalancing Charge | Metered energy |  |  |  |  | 0.002 | 0.002 | 0.017 | 0.069 | 0
Voltage Control Charge | Metered energy |  |  |  |  | 0.01 | 0.08 | 0.09 | 0.06 | 0
Other System Support Services Charge | Highest metered demand |  |  |  |  | 25 | 24 | 24 | 52 | 0
Other System Support Services Charge | Regulated Generating Unit Connection Cost |  |  |  |  | 0 | 0 | 0 | 0 | 0
Other System Support Services Charge | Apparent Power Difference |  |  |  |  | 400 | 400 | 400 | 400 | 0
Rider F | Rider F |  |  |  |  | 2.3 | 2.2 | 2.2 | 1.3 | 1.3
Revenue Offsets (Rate DOS) (Bulk - Fixed) | Metered energy | [8 empty] | 3.472 | 20%
Revenue Offsets (Rate DOS) (Regional - Fixed) | Metered energy | [8 empty] | 1.582
Total DOS Rate | [9 empty] | 7.194
| Year | Hours
| 2024 | 8784
| 2023 | 8760
| 2022 | 8760
| 2021 | 8760
| 2020 | 8784