PRC-002-AB-2

Disturbance Monitoring and Reporting Requirements

Effective Date: October 1, 2019

# Audit Summary

| Registered Entity: | [Registered Entity name as it appears in the AESO ARS Registry] |  |
| --- | --- | --- |
| Functional Entity: | [Functional entities for which the Registered Entity above was registered throughout the audit period] |  |
| Audit Period: | From: [Audit start date or standard effective date, whichever comes later] To: [Audit end date or standard withdrawal/supersede date, whichever comes first] |  |
| Audit: | [Scheduled (YYYY-QX) or Spot Check YYYY-MM-DD] |  |
| Compliance Monitoring Entity: | Alberta Electric System Operator (AESO) |  |
| Suspected Non-Compliance to the standard? |  |  |
|  |  | [If Yes, list the requirements with suspected contravention findings e.g. R1, R2, R7] |
| Date of Completion: | [Use YYYY-MM-DD format] |  |

## Assessment Commentary

[Information (if any) relevant to audit findings below]

## Findings

| R1 | [Summary of Findings] |
| --- | --- |
| R2 | [Summary of Findings] |
| R3 | [Summary of Findings] |
| R4 | [Summary of Findings] |
| R6 | [Summary of Findings] |
| R7 | [Summary of Findings] |
| R8 | [Summary of Findings] |
| R9 | [Summary of Findings] |
| R10 | [Summary of Findings] |
| R11 | [Summary of Findings] |
| R12 | [Summary of Findings] |

## Contact Information

| Audited Entity |  |  |
| --- | --- | --- |
| Compliance Primary | [Name] [Title] [Phone] [Email] |  |
| Subject Matter Expert | [Name] [Title] [Phone] [Email] |  |
| AESO Team |  | Sign-off |
| Lead Auditor | [Name] [Title] [Phone] [Email] | Date: Signature: |
| Auditor | [Name] [Title] [Phone] [Email] | Date: Signature: |
| Compliance Manager | [Name] [Title] [Phone] [Email] | Date: Signature: |
| Standard Owner | [Name] [Title] [Phone] [Email] | Date: Signature: |

# Applicability

This reliability standard applies to the following:

- the legal owner of a transmission facility that is part of the bulk electric system;

- the legal owner of a generating unit that is part of the bulk electric system;

- the legal owner of an aggregated generating facility that is part of the bulk electric system; and

- the ISO.

# Compliance Assessment

| # Requirement & Measure | Evidence Submission | Evidence Description | Evidence | Assessment Approach | Auditor Notes |
| --- | --- | --- | --- | --- | --- |
| R1 Each legal owner of a transmission facility must: R1.1 identify bulk electric system buses for which sequence of events recording and fault recording data is required by using the methodology in Appendix 1; R1.2 notify other legal owners of system elements on the bulk electric system connected to those bulk electric system buses, if any, within 90 days of completion of requirement R1.1, that those system elements require either one or both of sequence of events recording data and fault recording data; and R1.3 re-evaluate all bulk electric system buses at least once every 5 calendar years in accordance with requirement R1.1 and notify other legal owners, if any, in accordance with requirement R1.2, and implement the re-evaluated list of bulk electric system buses as per the Implementation Plan in Appendix 2. MR1 Evidence of identifying bulk electric system buses, notifying legal owners, re-evaluating all bulk electric system buses, and implementing the re-evaluated list as required in requirement R1 exists. Evidence may include lists, dated correspondence, or other equivalent evidence. | AR1 Please provide: | [Click and edit to enter description for AR1(i) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR1 (i) lists for appropriateness and completeness. | [For AESO use only] |
|  | - The dated list(s) of bulk electric system buses as specified in R1.1. |  |  |  |  |
|  | Dated evidence of identification as per R1.1. | [Click and edit to enter description for AR1(ii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR1 (ii) evidence to verify whether the methodology in Appendix 1 was applied. | [For AESO use only] |
|  | The dated list(s) of system elements and legal owners of each system element as specified in R1.2. | [Click and edit to enter description for AR1(iii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR (iii) evidence to verify whether all system elements connected to the buses identified in R1.1 and their legal owner are specified. | [For AESO use only] |
|  | Dated evidence of notification as per R1.2. | [Click and edit to enter description for AR1(iv) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR1 (ii), AR1 (iii), and AR1 (iv) evidence to determine whether a notification was sent to the legal owners of system elements identified as per R1.2. | [For AESO use only] |
|  | Dated evidence of re-evaluation, notification and implementation as per R1.3. | [Click and edit to enter description for AR1(v) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR1 (ii) and AR1 (v) dates to determine whether the list of bulk electric system buses identified as per R1.1 was re-evaluated at least once every 5 calendar years. Review AR1 (iii) and AR1 (v) to determine if notification was sent to other legal owners of system elements for the re-evaluated list. Review AR1 (v) evidence to determine whether revisions were implemented as per the Implementation Plan found in Appendix 2 | [For AESO use only] |
|  | or any other evidence to demonstrate compliance to R1. | [Click and edit to enter description for any other submitted evidence] | [Click and edit to embed file or link to evidence] | Review additional evidence provided. | [For AESO use only] |
| Findings |  |  |  |  |  |
| [For AESO use only] |  |  |  |  |  |

| # Requirement & Measure | Evidence Submission | Evidence Description | Evidence | Assessment Approach | Auditor Notes |
| --- | --- | --- | --- | --- | --- |
| R2 Each legal owner of a transmission facility, legal owner of a generating unit, and legal owner of an aggregated generating facility must have sequence of events recording data for circuit breaker position, open or close, for each circuit breaker it owns connected directly to the bulk electric system buses identified in requirement R1 and associated with the system elements on the bulk electric system at those bulk electric system buses. MR2 Evidence of having sequence of events recording data for circuit breaker positions as required in requirement R2 exists. Evidence may include documents describing the device interconnections and configurations which may include a single design standard as representative for common installations, station drawings, and data recordings, or other equivalent evidence. | AR2 Please provide: | [Click and edit to enter description for AR2(i) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR2 (i) list for completeness and correctness. | [For AESO use only] |
|  | - A list of circuit breakers as specified in R2. |  |  |  |  |
|  | Evidence describing the device’s interconnection or configuration to record data as per R2. - This may include design standards, station drawings or equivalent evidence. | [Click and edit to enter description for AR2(ii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR2 (ii) to verify that the device is configured to record circuit breaker position as per R2 for circuit breakers listed in AR2 (i) | [For AESO use only] |
|  | Actual sequence of events recording data pertaining to R2 recorded during the audit period. | [Click and edit to enter description for AR2(iii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR2 (iii) to verify that fault recording data exists and verify whether the open or close positions are recorded in the sequence of events recording data. | [For AESO use only] |
|  | or any other evidence to demonstrate compliance to R2. | [Click and edit to enter description for any other submitted evidence] | [Click and edit to embed file or link to evidence] | Review additional evidence provided. | [For AESO use only] |
| Findings |  |  |  |  |  |
| [For AESO use only] |  |  |  |  |  |

| # Requirement & Measure | Evidence Submission | Evidence Description | Evidence | Assessment Approach | Auditor Notes |
| --- | --- | --- | --- | --- | --- |
| R3 Each legal owner of a transmission facility, legal owner of a generating unit, and legal owner of an aggregated generating facility must have fault recording data to determine the following electrical quantities for each triggered fault recording for the system elements on the bulk electric system it owns connected to the bulk electric system buses identified in requirement R1: R3.1 phase-to-neutral voltage for each phase of each specified bulk electric system bus; and R3.2 each phase current and the residual or neutral current for the following system elements on the bulk electric system: R3.2.1 transformers that have a low-side operating voltage of 100 kV or above; and R3.2.2 transmission lines. MR3 Evidence of having fault recording data as required in requirement R3 exists. Evidence may include documents describing the device specifications and configurations which may include a single design standard as representative for common installations, station drawings, and data recordings, or other equivalent evidence. | AR3 Please provide: | [Click and edit to enter description for AR3(i) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR3 (i) list for completeness and correctness. | [For AESO use only] |
|  | - A list of system elements as specified in R3. |  |  |  |  |
|  | Evidence describing the device’s specifications or configuration to record data as per R3. - This may include a design standard, station drawings or equivalent evidence. | [Click and edit to enter description for AR3(ii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR3 (ii) to verify that the device records fault data which can be used to determine electrical quantities as per R3. | [For AESO use only] |
|  | The method(s) used to determine R3.1 and R3.2 including calculations, if used. | [Click and edit to enter description for AR3(iii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR3 (iii) and AR3 (ii) to verify if the electrical quantities in R3.1 and R3.2 can be determined using the methodology and the recording data. | [For AESO use only] |
|  | Actual fault recording data pertaining to R3 recorded during the audit period and electrical quantities as per R3.1 and R3.2. - If no triggered fault recording occurred during the audit period, provide an attestation letter to this effect. | [Click and edit to enter description for AR3(iv) submitted evidence] | [Click and edit to embed file or link to evidence] | If a fault recording was triggered during the audit period, review AR3 (iv) to verify the existence of fault recording data and whether the method found in AR3 (iii) is used to obtain the actual electrical quantities from the data. If an attestation letter is provided review the letter for completeness and correctness. | [For AESO use only] |
|  | or any other evidence to demonstrate compliance to R3. | [Click and edit to enter description for any other submitted evidence] | [Click and edit to embed file or link to evidence] | Review additional evidence provided. | [For AESO use only] |
| Findings |  |  |  |  |  |
| [For AESO use only] |  |  |  |  |  |

| # Requirement & Measure | Evidence Submission | Evidence Description | Evidence | Assessment Approach | Auditor Notes |
| --- | --- | --- | --- | --- | --- |
| R4 Each legal owner of a transmission facility, legal owner of a generating unit, and legal owner of an aggregated generating facility must have fault recording data as specified in requirement R3 that meets the following: R4.1 a single record or multiple records that include: (a) a pre-trigger record length of at least 2 cycles and a total record length of at least 30 cycles for the same trigger point, or (b) at least 2 cycles of the pre-trigger data, the first 3 cycles of the post-trigger data, and the final cycle of the fault as seen by the fault recorder; R4.2 a minimum recording rate of 16 samples per cycle; and R4.3 trigger settings for at least the following: R4.3.1 neutral (residual) overcurrent; and R4.3.2 phase under voltage or overcurrent. MR4 Evidence of having fault recording data as required in requirement R4 exists. Evidence may include data recordings, technical specification sheets, settings documentation, or other equivalent evidence. | AR4 Please provide: | [Click and edit to enter description for AR4(i) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR4 (i) to verify whether the device is configured as per R4.1. | [For AESO use only] |
|  | - Evidence of the device’s configuration as per R4.1. - This may include setting documentation or equivalent evidence. |  |  |  |  |
|  | Evidence of the device’s specification(s) as per R4.2. - This may include technical specification sheets, setting documentation or equivalent evidence. | [Click and edit to enter description for AR4(ii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR4 (ii) to verify whether the device specifications or configuration is as per R4.2. | [For AESO use only] |
|  | Evidence of the recording device’s configuration as per R4.3. - This may include setting documentation or equivalent evidence. | [Click and edit to enter description for AR4(iii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR4 (iii) to verify whether the device is configured as per R4.3. | [For AESO use only] |
|  | Actual fault recording data pertaining to R4 recorded during the audit period. - If no triggered fault recording occurred during the audit period, provide an attestation letter to this effect. | [Click and edit to enter description for AR4(iv) submitted evidence] | [Click and edit to embed file or link to evidence] | If a fault recording was triggered during the audit period, review AR4 (iv) to verify the existence of fault recording data which meets R4.1, R4.2 and R4.3. If an attestation letter is provided review the letter for completeness and correctness. | [For AESO use only] |
|  | or any other evidence to demonstrate compliance to R4. | [Click and edit to enter description for any other submitted evidence] | [Click and edit to embed file or link to evidence] | Review additional evidence provided. | [For AESO use only] |
| Findings |  |  |  |  |  |
| [For AESO use only] |  |  |  |  |  |

| # Requirement & Measure | Evidence Submission | Evidence Description | Evidence | Assessment Approach | Auditor Notes |
| --- | --- | --- | --- | --- | --- |
| R6 Each legal owner of a transmission facility must have dynamic disturbance recording data to determine the following electrical quantities for each system element on the bulk electric system it owns for which it received notification as identified in requirement R5: R6.1 one phase-to-neutral or positive sequence voltage; R6.2 the phase current for the same phase at the same voltage corresponding to the voltage in requirement R6.1, or the positive sequence current; R6.3 real power and reactive power flows expressed on a 3-phase basis corresponding to all circuits where current measurements are required; and R6.4 frequency of any one of the voltages in requirement R6.1. MR6 Evidence of having dynamic disturbance recording data as required in requirement R6 exists. Evidence may include data records, documents describing the device specifications and configurations, which may include a single design standard as representative for common installations, station drawings, or other equivalent evidence. | AR6 Please provide: | [Click and edit to enter description for AR6(i) submitted evidence] | [Click and edit to embed file or link to evidence] | Review the received information of ISO’s notification including the system element(s). If an attestation letter is provided review the letter for completeness and correctness. | [For AESO use only] |
|  | - The notifications received from the ISO during the audit period; - If no notifications were received from the ISO, please provide an attestation letter to this effect. |  |  |  |  |
|  | Evidence describing the device’s specifications or configuration to record data as per R6. - This may include a design standard, station drawings or equivalent evidence. | [Click and edit to enter description for AR6(ii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR6 (ii) to verify whether the device records dynamic disturbance recording data can be used to determine electrical quantities as per R6. | [For AESO use only] |
|  | The method(s) used to determine R6.1, R6.2, R6.3 and R6.4 including calculations, if used. | [Click and edit to enter description for AR6(iii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR6 (iii) and AR6 (ii) to verify if the electrical quantities in R6.1, R6.2, R6.3 and R6.4 can be determined using the methodology and the dynamic disturbance recording data. | [For AESO use only] |
|  | Actual dynamic disturbance recording data pertaining to R6 recorded during the audit period, and electrical quantities as per R6.1, R6.2, R6.3 and R6.4. | [Click and edit to enter description for AR6(iv) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR6 (iv) to verify the existence of dynamic disturbance recording data as per R6. Verify whether the method found in AR6 (iii) is used to obtain the actual electrical quantities from the recording data. | [For AESO use only] |
|  | or any other evidence to demonstrate compliance to R6. | [Click and edit to enter description for any other submitted evidence] | [Click and edit to embed file or link to evidence] | Review additional evidence provided. | [For AESO use only] |
| Findings |  |  |  |  |  |
| [For AESO use only] |  |  |  |  |  |

| # Requirement & Measure | Evidence Submission | Evidence Description | Evidence | Assessment Approach | Auditor Notes |
| --- | --- | --- | --- | --- | --- |
| R7 Each legal owner of a generating unit and legal owner of an aggregated generating facility must have dynamic disturbance recording data to determine the following electrical quantities for each system element on the bulk electric system it owns for which it received notification as identified in requirement R5: R7.1 one phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer high-side or low-side voltage level; R7.2 the phase current for the same phase at the same voltage corresponding to the voltage in requirement R7.1, phase currents for any phase-to-phase voltages, or positive sequence current; R7.3 real power and reactive power flows expressed on a 3-phase basis corresponding to all circuits where current measurements are required; and R7.4 frequency of at least one of the voltages in requirement R7.1. MR7 Evidence of having dynamic disturbance recording data as required in requirement R7 exists. Evidence may include data records, documents describing the device specifications and configurations, which may include a single design standard as representative for common installations, station drawings, or other equivalent evidence. | AR7 Please provide: | [Click and edit to enter description for AR7(i) submitted evidence] | [Click and edit to embed file or link to evidence] | Review the received information of ISO’s notifications including the system element(s). If an attestation letter is provided review the letter for completeness and correctness. | [For AESO use only] |
|  | - The notifications received from the ISO during the audit period; - If no notifications were received from the ISO, please provide an attestation letter to this effect. |  |  |  |  |
|  | Evidence describing the recording device’s specifications or configuration to record data as per R7. - This may include a design standard, station drawings or equivalent evidence. | [Click and edit to enter description for AR7(ii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR7 (ii) to verify whether the device records dynamic disturbance recording data which can be used to determine electrical quantities as per R7. | [For AESO use only] |
|  | The method(s) used to determine R7.1, R7.2, R7.3 and R7.4 including calculations, if used. | [Click and edit to enter description for AR7(iii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR7 (iii) and AR7 (ii) to verify if the electrical quantities in R7.1, R7.2, R7.3 and R7.4 can be determined using the methodology and the dynamic disturbance recording data. | [For AESO use only] |
|  | Actual dynamic disturbance recording data pertaining to R7 recorded during the audit period and electrical quantities as per R7.1, R7.2, R7.3 and R7.4. | [Click and edit to enter description for AR7(iv) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR7 (iv) to verify the existence of dynamic disturbance recording data as per R7. Verify whether the method found in AR7 (iii) is used to obtain the actual electrical quantities from the recording data. | [For AESO use only] |
|  | or any other evidence to demonstrate compliance to R7. | [Click and edit to enter description for any other submitted evidence] | [Click and edit to embed file or link to evidence] | Review additional evidence provided. | [For AESO use only] |
| Findings |  |  |  |  |  |
| [For AESO use only] |  |  |  |  |  |

| # Requirement & Measure | Evidence Submission | Evidence Description | Evidence | Assessment Approach | Auditor Notes |
| --- | --- | --- | --- | --- | --- |
| R8 Each legal owner of a transmission facility, legal owner of a generating unit, and legal owner of an aggregated generating facility responsible for dynamic disturbance recording data for the system elements on the bulk electric system for which it received notification as identified in requirement R5 must, unless it complies with subsection 7(1) of Section 502.9 of the ISO rules, Synchrophasor Measurement Unit Technical Requirements, have continuous data recording and storage, unless the equipment was installed prior to the effective date of this reliability standard and is not capable of continuous recording, in which case, triggered records must meet the following: R8.1 triggered record lengths of at least 3 minutes; or R8.2 at least one of the following 3 triggers: (a) off nominal low frequency trigger set at < 59.55 Hz and off nominal high frequency trigger set at > 61.0 Hz; (b) rate of change of frequency trigger set at < 0.05625 Hz/sec and > 0.125 Hz/sec; or (c) undervoltage trigger set no lower than 85% of normal operating voltage for a duration of 5 seconds. MR8 Evidence of having continuous data recording and storage, or of having triggered records that meet the criteria required in requirement R8 exists. Evidence may include data recordings, technical specification sheets, settings documentation, or other equivalent evidence. | AR8 Please provide: | [Click and edit to enter description for AR8(i) submitted evidence] | [Click and edit to embed file or link to evidence] | Review the received information of ISO’s notifications including the system element(s). If an attestation letter is provided review the letter for completeness and correctness. | [For AESO use only] |
|  | - The notifications received from the ISO during the audit period; - If no notifications were received from the ISO, please provide an attestation letter to this effect. |  |  |  |  |
|  | Installation date for each dynamic disturbance recording equipment; | [Click and edit to enter description for AR8(ii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review the date of installation for each dynamic disturbance recording equipment. | [For AESO use only] |
|  | Evidence describing the recording device’s specifications or configuration to record and store data as per R8 including evidence that the device: - Complies with subsection 7(1) of Section 502.9 of the ISO rules, if appropriate; or - Has continuous data recording and storage; or - Records as per R8.1 or R8.2 if the equipment was installed prior to effective date of the standard and is not capable of continuous recording. | [Click and edit to enter description for AR8(iii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR8 (iii) to verify whether the device has continuous data recording and storage or is not capable of continuous recording, as per R8. If the device complies with subsection 7(1) of Section 502.9 of the ISO rules, review AR8 (iii) for appropriateness. For equipment that was installed prior to the effective date of the standard and is not capable of continuous data recording, review AR8 (iii) to verify that the equipment is configured as per R8.1 or R8.2. | [For AESO use only] |
|  | Actual dynamic disturbance recording data pertaining to R8 recorded during the audit period. | [Click and edit to enter description for AR8(iv) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR8 (iv) to verify the existence of dynamic disturbance recording data as per R8. For equipment installed prior to the effective date of the standard and not capable of continuous data recording, review AR8 (v) to verify records as per R8.1 or R8.2. | [For AESO use only] |
|  | or any other evidence to demonstrate compliance to R8. | [Click and edit to enter description for any other submitted evidence] | [Click and edit to embed file or link to evidence] | Review additional evidence provided. | [For AESO use only] |
| Findings |  |  |  |  |  |
| [For AESO use only] |  |  |  |  |  |

| # Requirement & Measure | Evidence Submission | Evidence Description | Evidence | Assessment Approach | Auditor Notes |
| --- | --- | --- | --- | --- | --- |
| R9 Each legal owner of a transmission facility, legal owner of a generating unit, and legal owner of an aggregated generating facility responsible for dynamic disturbance recording data for the system elements on the bulk electric system identified in requirement R5 must have dynamic disturbance recording data that meet the following: R9.1 input sampling rate of at least 960 samples per second; and R9.2 output recording rate of electrical quantities of at least 30 times per second. MR9 Evidence of having dynamic disturbance recording data as required in requirement R9 exists. Evidence may include data recordings, technical specification sheets, settings documentation or other equivalent evidence. | AR9 Please provide: | [Click and edit to enter description for AR9(i) submitted evidence] | [Click and edit to embed file or link to evidence] | Review the received information of ISO’s notifications including the system element(s) specified. If an attestation letter is provided review the letter for completeness and correctness. | [For AESO use only] |
|  | - The notifications received from the ISO during the audit period; - If no notifications were received from the ISO, please provide an attestation letter to this effect. |  |  |  |  |
|  | Evidence describing the recording device’s specifications or configuration as per R9. | [Click and edit to enter description for AR9(ii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR9 (ii) to verify whether the dynamic disturbance recording data meets the technical specifications as per R9.1 and R9.2. | [For AESO use only] |
|  | Actual dynamic disturbance recording data pertaining to R9 recorded during the audit period. | [Click and edit to enter description for AR9(iii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR9 (iii) to verify the existence of dynamic disturbance recording data as per R9 and whether the data meets the technical specifications as per R9.1 and R9.2. | [For AESO use only] |
|  | or any other evidence to demonstrate compliance to R9. | [Click and edit to enter description for any other submitted evidence] | [Click and edit to embed file or link to evidence] | Review additional evidence provided. | [For AESO use only] |
| Findings |  |  |  |  |  |
| [For AESO use only] |  |  |  |  |  |

| # Requirement & Measure | Evidence Submission | Evidence Description | Evidence | Assessment Approach | Auditor Notes |
| --- | --- | --- | --- | --- | --- |
| R10 Each legal owner of a transmission facility, legal owner of a generating unit, and legal owner of an aggregated generating facility must time synchronize all sequence of events recording and fault recording data for the bulk electric system buses identified in requirement R1 and dynamic disturbance recording data for the system elements on the bulk electric system identified in requirement R5 to meet the following: R10.1 synchronization to Coordinated Universal Time with or without a local time offset; and R10.2 synchronized device clock accuracy within ± 2 milliseconds of Coordinated Universal Time. MR10 Evidence of time synchronizing all sequence of events recording and fault recording data, and dynamic disturbance recording data as required in requirement R10 exists. Evidence may include technical specification sheets, settings documentation, or other equivalent evidence. | AR10 Please provide: | [Click and edit to enter description for AR10(i) submitted evidence] | [Click and edit to embed file or link to evidence] | Review the received information of ISO’s notifications including the system element(s) specified.. If an attestation letter is provided review the letter for completeness and correctness. | [For AESO use only] |
|  | - The notifications received from the ISO during the audit period; - If no notifications were received from the ISO, please provide an attestation letter to this effect |  |  |  |  |
|  | Evidence describing the recording device’s specifications or configuration as per R10. | [Click and edit to enter description for AR10(ii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR10 (ii) to verify that the device’s time synchronization meets R10.1 and R10.2. | [For AESO use only] |
|  | Actual dynamic disturbance recording data, sequence of events recording data and fault recording data recorded during the audit period as per R10. | [Click and edit to enter description for AR10(iii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR10(iii) to verify that dynamic disturbance recording data, sequence of event recording data, and fault recording data was time synchronized as per R10.1 and R10.2. | [For AESO use only] |
|  | or any other evidence to demonstrate compliance to R10. | [Click and edit to enter description for any other submitted evidence] | [Click and edit to embed file or link to evidence] | Review additional evidence provided. | [For AESO use only] |
| Findings |  |  |  |  |  |
| [For AESO use only] |  |  |  |  |  |

| # Requirement & Measure | Evidence Submission | Evidence Description | Evidence | Assessment Approach | Auditor Notes |
| --- | --- | --- | --- | --- | --- |
| R11 Each legal owner of a transmission facility, legal owner of a generating unit, and legal owner of an aggregated generating facility must provide to the ISO, upon written request, all sequence of events recording and fault recording data for the bulk electric system buses identified in requirement R1 and dynamic disturbance recording data for the system elements on the bulk electric system identified in requirement R5, in accordance with the following: R11.1 data is retrievable for the period of 10 days, inclusive of the day the data was recorded; R11.2 data subject to requirement R11.1 is provided within 30 days of a request unless an extension is granted by the ISO; R11.3 sequence of events recording data are provided in ASCII Comma Separated Value format following Appendix 3; R11.4 fault recording and dynamic disturbance recording data are provided in electronic files that are formatted in conformance with C37.111, IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later; and R11.5 data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. MR11 Evidence of providing all sequence of events recording and fault recording data as required in requirement R11 exists. Evidence may include dated correspondence, documents describing data storage capability, device specification, configuration or settings, data records, or other equivalent evidence. | AR11 Please provide: | [Click and edit to enter description for AR11(i) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR11 (i) including the dates of the request and the information requested by the ISO If an attestation letter is provided review the letter for completeness and correctness. | [For AESO use only] |
|  | - The written requests from the ISO during the audit period for sequence of events recording, fault recording and/or dynamic disturbance recording data; - If no requests were received from the ISO, please provide an attestation letter to this effect; |  |  |  |  |
|  | Evidence that the data for sequence of events recording, fault recording, and dynamic disturbance recording data is retrievable as per R11.1. | [Click and edit to enter description for AR11(iii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR11 (ii) to verify whether the data is retrievable for the period of 10 days, inclusive of the day the data was recorded. | [For AESO use only] |
|  | The recording data files requested by the ISO and dated evidence that the data files were sent to the ISO. | [Click and edit to enter description for AR11(iv) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR11 (iii) to determine whether the data was provided to the ISO within 30 days of the ISO’s written request, unless an extension is granted by the ISO. Review the recording data files to verify whether R11.3 and/or R11.4 were met in accordance to the data type requested. Review the recording data files to verify whether data files are named as per R11.5. | [For AESO use only] |
|  | or any other evidence to demonstrate compliance to R11. | [Click and edit to enter description for any other submitted evidence] | [Click and edit to embed file or link to evidence] | Review additional evidence provided. | [For AESO use only] |
| Findings |  |  |  |  |  |
| [For AESO use only] |  |  |  |  |  |

| # Requirement & Measure | Evidence Submission | Evidence Description | Evidence | Assessment Approach | Auditor Notes |
| --- | --- | --- | --- | --- | --- |
| R12 Each legal owner of a transmission facility, legal owner of a generating unit, and legal owner of an aggregated generating facility must, within 90 days of the discovery of a failure of the recording capability for the sequence of events recording, fault recording or dynamic disturbance recording data, either: (a) restore the recording capability, or (b) submit a corrective action plan to the ISO and implement it. MR12 Evidence of either restoring the recording capability or submitting a corrective action plan and implementing it as required in requirement R12 exists. Evidence may include dated reports of discovery of a failure, documentation noting the date the data recording was restored, SCADA records, work orders, dated correspondence, a corrective action plan, or other equivalent evidence. | AR12 Please provide: | [Click and edit to enter description for AR12(i) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR12 (i) including the date the failure was discovered. If an attestation letter is provided review the letter for completeness and correctness. | [For AESO use only] |
|  | - A list of failures of recording capability as per R12 which occurred during the audit period, including the date the failure occurred, if known, and the date the failure was discovered; - If no failures as specified in R12 occurred during the audit period, please provide an attestation letter to this effect. |  |  |  |  |
|  | Dated evidence of restoring the recording capability or submission of a corrective action plan to the ISO including corrective actions and target completion dates. | [Click and edit to enter description for AR12(ii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR12 (ii) to verify whether the failure of recording capability was restored in 90 calendar days from the discovery date of the failure or a corrective action plan was submitted to the ISO within 90 calendar days from the discovery date of the failure. | [For AESO use only] |
|  | Evidence that the corrective action plans were implemented, including the date that the corrective action plan was completed; - If any corrective action plans are in the process of being implemented, please provide details, including the estimated implementation date. | [Click and edit to enter description for AR12(iii) submitted evidence] | [Click and edit to embed file or link to evidence] | Review AR12 (iii) to verify whether the corrective action plans were implemented. | [For AESO use only] |
|  | or any other evidence to demonstrate compliance to R12. | [Click and edit to enter description for any other submitted evidence] | [Click and edit to embed file or link to evidence] | Review additional evidence provided. | [For AESO use only] |
| Findings |  |  |  |  |  |
| [For AESO use only] |  |  |  |  |  |

# General Notes

The AESO developed this Reliability Standard Audit Worksheet (RSAW) to add clarity and consistency to the audit team’s assessment of compliance with this reliability standard, including the approach elected to assess requirements.

Additionally, the RSAW provides a non-exclusive list of examples of the types of evidence a market participant may produce or may be asked to produce to demonstrate compliance with this reliability standard. A market participant’s adherence to the examples contained within this RSAW does not constitute compliance with the reliability standard.

This document is not an AESO authoritative document and revisions to it may be made from time to time by the AESO. Market participants are notified of revisions through the stakeholder update process.

# Notes to File

[For AESO use only: any observations, remarks or action items for future audits]

# Revision History

| Version | Issue Date | Description |
| --- | --- | --- |
| 1.0 | June 14, 2019 | Initial version of Worksheet |

Evidence may be provided for the entire population in the initial evidence submission at the Entity’s discretion. Otherwise, the AESO will request specific samples.

Evidence may be provided for the entire population in the initial evidence submission at the Entity’s discretion. Otherwise, the AESO will request specific samples.

Evidence may be provided for the entire population in the initial evidence submission at the Entity’s discretion. Otherwise, the AESO will request specific samples.

Evidence may be provided for the entire population in the initial evidence submission at the Entity’s discretion. Otherwise, the AESO will request specific samples.

Evidence may be provided for the entire population in the initial evidence submission at the Entity’s discretion. Otherwise, the AESO will request specific samples.

Evidence may be provided for the entire population in the initial evidence submission at the Entity’s discretion. Otherwise, the AESO will request specific samples.

Evidence may be provided for the entire population in the initial evidence submission at the Entity’s discretion. Otherwise, the AESO will request specific samples.

Evidence may be provided for the entire population in the initial evidence submission at the Entity’s discretion. Otherwise, the AESO will request specific samples